## Bomba Isla
|  | HOJA DE DATOS | [13 empty] | No.:
HD
|  | Proyecto: | PROVISIÓN DE EQUIPOS PARA MANGA DE CARGUÍO EN TERMINAL ARICA | [12 empty] | Hoja:
[18 empty] | 1 | de | 2
|  | Titulo.: HOJA DE DATOS P-6300 | HOJA DE DATOS DE ELECTROBOMBA
EQUIPO |  | TAG |  | P-XXXX | [6 empty] | Fabricante |  |  | M. SCHMITT & CIA / FLOWSERVE ó SIMILAR
|  | Descripción |  | Centrifugal Pump | [6 empty] | Modelo |  |  | 196 MT / DURCO MARK 3 ó SIMILAR
|  | Servicio |  | Carguío de DIESEL OIL/GE/CRUDO a Cisternas | [6 empty] | Serial |  |  | -
PERFORMANCE DATA | DESIGN/PROCESS CONDITIONS | Fluid Name | [5 empty] | DIESEL OIL/GE/CRUDO |  | ACTUAL PUMP PERFORMANCE | [6 empty] | DESIGN |  | MAXIMUM
|  | Fluid Capacity (Actual) |  |  |  |  | gpm | 300 |  |  | Fluid capacity (Actual) |  |  |  | gpm |  | 300 |  | 600
|  | Fluid Capacity (Standard) |  |  |  |  | sgpm | 300 |  |  | Fluid Capacity (Standard) |  |  |  | sgpm |  | by vendor |  | by vendor
|  | Specific Gravity |  |  |  |  | S.G. | 0,88/0,72 |  |  | Fluid Minimun Flow |  |  |  | gpm |  | by vendor |  | by vendor
|  | Fluid Density |  |  |  |  | gr./cc | 0.8 |  |  | Discharge Temperature |  |  |  | °F |  | 77.15 |  | -
|  | Viscosity |  |  |  |  | cp | 0,516/7,35/0,564 |  |  | Suction Pressure |  |  |  | psig |  | - |  | -
|  | Vapor Pressure |  |  |  |  | psia | 0,02/0,729/0,716 |  |  | Discharge Pressure |  |  |  | psig |  | 40 |  | 45.44
|  | Suction Temperature |  |  |  |  | °F | 70
|  | TDH MIN |  |  |  |  | ft | 105 |  |  | Pump Efficiency |  |  |  | % |  | by vendor |  | by vendor
|  | Suction Pressure (Normal) |  |  |  |  | psig | -2.3 |  |  | Maximum BHP W/Rated Imp. |  |  |  | hp |  | by vendor |  | -
|  | Suction Pressure (Max) |  |  |  |  | psig | 0.15 |  |  | Maximum Head W/Rated Imp. |  |  |  | ft |  | by vendor |  | -
|  | Discharge Pressure |  |  |  |  | psig | 40
|  | NPSH (Available) |  |  |  |  | ft | 7.5 |  |  | NPSH (Required) |  |  |  | ft |  | 3.1 |  | by vendor
DESIGN - MATERIAL CONSTRUCTION | PUMP | Model |  |  |  | by vendor |  | MATERIAL | Casing |  | Carbon Steel A216 |  |  | ELECTRIC MOTOR | Manufacturer
|  | Size |  |  |  | 4x3 |  |  | Impeller |  | 12% Chrome Steel A487 |  |  |  | Motor Type
|  | Max Pressure | [6 empty] | Pump Shaft |  | 4140 Steel A434 4140 |  |  |  | Frame
|  | N° Stages |  |  |  | 1 |  |  | Pump Support Plate |  | yes |  |  |  | HP Rating |  |  | 15 HP @ 1500 RPM
|  | Impeller Size |  |  |  | by vendor |  |  | Case W.R. |  | 410 SS A426 CPCA15 |  |  |  | Volt/Phase/Hz |  |  | 380 / 3 / 50
[9 empty] | Impeller W. R. |  | 410 SS A426 CPCA15 |  |  |  | Enclosure |  |  | Class 1 Div 1 Gr D
|  | Casing type | [6 empty] | Throat Bushing | [5 empty] | Bearings
|  | Nozzle | Suction |  | Discharge |  |  |  | Pit Depth | [5 empty] | Lubrication |  |  | Grease
|  | Size | 4" |  | 3" | [9 empty] | Insulation |  |  | F
|  | ANSI | 150 |  | 150 | [9 empty] | Full Laod Amp
|  | Facing | RF |  | RF | [9 empty] | Protection Level |  |  | IP 55 (min.)
|  | Location | 0° |  | 90º
AUXILIARY | SHOP TESTS | Hidrostatic |  |  |  | YES |  | SHIPPING INFORMATION | Weight Pump & Bass |  |  | Lbm
|  | Test Pressure psig | [6 empty] | Weight Motor |  |  | Lbm
|  | Perfonmance Test | [6 empty] | Total Shipping Weight |  |  | Lbm
|  | Test NPSH ft. | [6 empty] | Dimension (L x W x H) |  |  | in
|  | Shop Inspection |  |  |  | N/R |  |  | Acople |  |  |  | Acoplamiento flexible marca John Crane, KTR o similar
Notes:
1.- ANSI B71.3M o API 610 required
2.- In Q/H curve, rated condition point shall be as close as possible of BEP and always between BEP and shut-off condition
3.- Shut-off Head shall be between 105% and 130% of Rated Head
4.- NPSHR shall be at lest 1 ft lower than NPSHA

## Bomba Isla
| HOJA DE DATOS |  | No.:
HD
| Proyecto: | PROVISIÓN DE EQUIPOS PARA MANGA DE CARGUÍO EN TERMINAL ARICA | Hoja:
|  |  |  | 2 | de | 2
| Titulo.: HOJA DE DATOS P-6300 | HOJA DE DATOS DE ELECTROBOMBA
REFERENCIA FOTOGRÁFICA QUE DEBE CUMPLIR LA BOMBA REQUERIDA
Electrobomba existente, el requerimiento corresponde a 1 pieza de equipo similar.
Curva Característica y Placa de Bomba Existente